## Slide 1
IEEE Baton Rouge
Grounding for Electrical Power Systems (Low Resistance and High Resistance Design)

## Slide 2: Overview
Low Resistance Grounding
  Advantages/Disadvantages
  Design Considerations
High Resistance Grounding
  Advantages/Disadvantages
  Design Considerations
Generator Grounding
  Single/Multiple arrangements

## Slide 3: Low Resistance Grounding

## Slide 4: Low Resistance Grounding
Impedance selected to limit line-to-ground fault current (normally between 100A and 1000A as defined by IEEE std. 142-2007 section 1.4.3.2)

## Slide 5: Low Resistance Grounding
Advantages
  Eliminates high transient overvoltages
  Limits damage to faulted equipment
  Reduces shock hazard to personnel
Disadvantages
  Some equipment damage can still occur
  Faulted circuit must be de-energized
  Line-to-neutral loads cannot be used.
c
c
c
I
a
b
I
I
c
I
r
A
Ø
B
Ø
C
Ø
3Ø Load
or Network
Source
N
Neutral
Grounding
Resistor

## Slide 6: Low Resistance Grounding
Most utilized on Medium Voltage
  Some 5kV systems
  Mainly 15kV systems
  Has been utilized on up to 132kV systems (rare)
Used where system charging current may be to high for High Resistance Grounding
c
c
c
I
a
b
I
I
c
I
r
A
Ø
B
Ø
C
Ø
3Ø Load
or Network
Source
N
Neutral
Grounding
Resistor

## Slide 7: LRG Design Considerations
Resistor Amperage (ground fault let through current)
  System Capacitance
  System Bracing
System Insulation
Relay Trip points (Time current curve)
  Selective tripping
  Resistance increase with temperature
Resistor time on (how long the fault is on the system)
Single Phase Loads

## Slide 8: LRG Design Consideration: System Capacitance (Charging Current)
Conductor
Cable insulation
Cable tray
Every electrical system has some natural capacitance. The capacitive reactance of the system determines the charging current.
Zero-sequence Capacitance: µF/phase
Charging Current: A

## Slide 9: LRG Design Consideration: System Capacitance (Charging Current)

## Slide 10: LRG Design Consideration: System Capacitance (Charging Current)
During an arcing or intermittent fault, a voltage is held on the system capacitance after the arc is extinguished. This can lead to a significant voltage build-up which can stress system insulation and lead to further faults.
In a resistance grounded system, the resistance must be low enough to allow the system capacitance to discharge relatively quickly.
Only discharges if Ro < Xco, so Ir > Ixco
( per IEEE142-2007 1.2.7)
  That is, resistor current must be greater than capacitive charging current.

## Slide 11: LRG Design Considerations: System Bracing
Total Fault current is the vector sum of capacitive charging current and resistor current
So, if IR = IC0, then IF = 1.414 IR
Total fault current must not exceed the value for which the system is braced.
In many cases, the system is already braced for the three-phase fault current which is much higher than the single line-ground fault current of a resistance grounded system.

## Slide 12: LRG Design Considerations: System Insulation
Resistance grounded systems must be insulated for full line-line voltage with respect to ground.
Surge Arrestor Selection: NEC 280.4 (2) Impedance or Ungrounded System. The maximum continuous operating voltage shall be the phase-to-phase voltage of the system.
Cables: NEC Table 310.13E allows for use of 100% Insulation level, but 173% is recommended for orderly shutdown.
VAG
VBG
VCG
VAG
VBG
Un-faulted Voltages to ground
Faulted Voltages to ground (VCG = 0)

## Slide 13: LRG Design Considerations: System Insulation
Properly rated equipment prevents Hazards.
0V
2400V
Ground ≈ AØ
Cables, TVSSs, VFDs, etc. and other equipment must be rated for elevated voltages.
0V
4160V
4160V
NGR

## Slide 14: LRG Design Considerations: Relay Coordination: Selective tripping
N
G
R
CTs and relays must be designed such that system will trip on a fault of the magnitude of the ground fault current, but not on transient events such as large motor startup.
Network protection scheme should try to trip fault location first, then go upstream.

## Slide 15: LRG Design Considerations: Relay Coordination: Selective tripping
Residual connected CT’s
Zero Sequence CT

## Slide 16: LRG Design Considerations: Relay Coordination: Resistance Increase
Widely varying use of resistance material in the industry.
  Different coefficients of resistivity for these materials.
  Coefficient of resistivity typically increases with temperature of the material, thus resistance of the NGR increases while the unit runs.
  As resistance increases, current decreases.
  Relay current trip curve must fall below the current line in the graph below.
Chart: NGR Resistance vs Current
Current | 393.6786 | 383.0062 | 373.6333 | 365.7513 | 358.8398 | 352.5042 | 346.7303 | 342.0373 | 338.4203 | 335.6149
Resistance | 6.0963 | 6.2662 | 6.4234 | 6.5618 | 6.6882 | 6.8084 | 6.9218 | 7.0168 | 7.0918 | 7.1511

## Slide 17: LRG Design Considerations: Resistor time on
Normally, protective relaying will trip within a few cycles.
IEEE 32 defines standard resistor on times. Lowest rate is 10 seconds, but could potentially go less to save material/space.
Can go as high as 30 or 60 seconds as required (rare).
Extended or Continuous ratings are almost never used in this application due to the relatively high fault currents.
IEEE Std 32 | 
Time Rating and Permissible Temperature Rise for Neutral Grounding Resistors | 
Time Rating (On Time) | Temp Rise (deg C)
Ten Seconds (Short Time) | 760oC
One Minute (Short Time) | 760oC
Ten Minutes (Short Time) | 610oC
Extended Time | 610oC
Continuous | 385oC

## Slide 18: LRG Design Considerations: No Single Phase Loads
Phase and Neutral wires in same conduit. If faulted, bypass HRG, thus, Φ-G fault.
No line-to-neutral loads allowed, prevents Hazards.
NGR

## Slide 19: LRG Design Considerations: No Single Phase Loads
Add small 1:1 transformer and solidly ground secondary for 1Φ loads (i.e. lighting).

## Slide 20: High Resistance Grounding

## Slide 21: High Resistance Grounding
Impedance selected to limit line-to-ground fault current (normally < 10A as defined by IEEE std. 142-2007 section 1.4.3.1)
Ground detection system required
System is alarm and locate instead of trip.

## Slide 22: High Resistance Grounding
Advantages
  Eliminates high transient overvoltages
  Limits damage to faulted equipment
  Reduces shock hazard to personnel
  Faulted circuit allowed to continue operating
Disadvantages
  Nuisance alarms are possible.
  Line-to-neutral loads cannot be used.
c
c
c
I
a
b
I
I
c
I
r
A
Ø
B
Ø
C
Ø
3Ø Load
or Network
Source
N
Neutral
Grounding
Resistor

## Slide 23: High Resistance Grounding
Most utilized on Low Voltage
  Many 600V systems
  Some 5kV systems
  Has been utilized on up to 15kV systems (rare)
c
c
c
I
a
b
I
I
c
I
r
A
Ø
B
Ø
C
Ø
3Ø Load
or Network
Source
N
Neutral
Grounding
Resistor

## Slide 24: HRG Design Considerations
Resistor Amperage (ground fault let through current)
  System Capacitance
Alarm notification
Fault Location
  Pulsing
  Data Logging
Relay Coordination (What to do if there is a second fault)
System Insulation
Personnel training

## Slide 25: HRG Design Consideration: System Capacitance (Charging Current)
Conductor
Cable insulation
Cable tray
Every electrical system has some natural capacitance. The capacitive reactance of the system determines the charging current.
Zero-sequence Capacitance: µF/phase
Charging Current: A

## Slide 26: HRG Design Consideration: System Capacitance (Charging Current)
During an arcing or intermittent fault, a voltage is held on the system capacitance after the arc is extinguished. This can lead to a significant voltage build-up which can stress system insulation and lead to further faults.
In a resistance grounded system, the resistance must be low enough to allow the system capacitance to discharge relatively quickly.
Only discharges if Ro < Xco, so Ir > Ixco
( per IEEE142-2007 1.2.7)
  That is, resistor current must be greater than capacitive charging current.

## Slide 27: HRG Design Consideration: System Capacitance (Charging Current)
Major Contributors to system capacitance:
  Line-ground filters on UPS systems
  Line-ground smoothing capacitors
  Multiple sets of line-ground surge arrestors
All of these can make implementation of HRG difficult

## Slide 28: HRG Design Consideration: Alarm Notification
HRG systems are alarm and locate systems
Alarm methods:
  Audible horn
  Red “fault” light
  Dry contact to PLC/DCS/SCADA opens
  DCS/SCADA polling of unit via Modbus
    RS-485
    Ethernet

## Slide 29: HRG Design Consideration: Fault Location (Pulsing)
HRG
480V Wye Source
C
Ø
B
Ø
A
Ø
55.4
ohms
Operator controlled contactor shorts out part of the resistor
Ideally, the increase in current is twice that of the normal fault current, unless that level is unsafe.

## Slide 30: HRG Design Consideration: Fault Location (Pulsing)
NOTE: Tracking a ground fault can only be done on an energized system. Due to the inherent risk of electrocution this should only be performed by trained and competent personnel.

## Slide 31: HRG Design Consideration: Fault Location (Pulsing)
Meter reading will alternate from 5A to 10A every 2 seconds.
Alternatives to Manual location:
Add zero sequence CTs & ammeters to each feeder
Use metering inherent to each breaker (newer equipment only)

## Slide 32: HRG Design Consideration: Fault Location (Data Logging)
HRG systems with data logging can be used to locate intermittent ground faults
Example:
  Heater with ground fault comes on at 11:00am and then turns off at 11:01am
  Normal Pulsing will not locate since the fault will be “gone”.
  HRG Data logging can help locate faulted equipment in conjunction with DCS/SCADA data records
Chart: 

## Slide 33: HRG Design Considerations: Relay Coordination: Selective tripping
If there is a second ground fault on another phase, it is essentially a phase-phase fault and at least one feeder needs to trip
Network protection scheme should be designed to trip the lowest priority feeder first, then the next, and then move upstream.

## Slide 34: HRG Design Considerations: Relay Coordination: Selective tripping
Check MCC GF pickup ratings to be sure the small ground fault current values do not trip off the motor on the first ground fault.
Also, fusing on small motors can open during a ground fault. Consult NEC Table 430.52 for Percentage of full load current fuse ratings. Most are 300% FLC.

## Slide 35: HRG Design Considerations: System Insulation
Resistance grounded systems must be insulated for full line-line voltage with respect to ground.
NEC 285.3: An SPD (surge arrestor or TVSS) device shall not be installed in the following: (2) On ungrounded systems, impedance grounded systems, or corner grounded systems unless listed specifically for use on these systems.
VAG
VBG
VCG
VAG
VBG
Un-faulted Voltages to ground
Faulted Voltages to ground (VCG = 0)

## Slide 36: HRG Design Considerations: System Insulation
Properly rated equipment prevents Hazards.
0V
277V
Ground ≈ AØ
Cables, TVSSs, VFDs, etc. and other equipment must be rated for elevated voltages.
0V
480V
480V

## Slide 37: HRG Design Considerations: System Insulation
Common Mode Capacitors provide path for Common-mode currents in output motor leads
MOVs protect against Transients

## Slide 38
Ground fault in Drive #1 caused Drive 2 to fault on over-voltage
Drive 3 was not affected
HRG Design Considerations: System Insulation

## Slide 39: HRG Design Considerations: System Insulation
  Factory option codes exist to remove the internal jumpers

## Slide 40: HRG Design Considerations: Personnel Training
  Per NEC 250.36, personnel must be trained on Impedance Grounded systems.
  Training should:
    Establish seriousness of a fault
    Discuss location methods
    Familiarize personnel with equipment

## Slide 41: Generator Grounding

## Slide 42: Generator Considerations
Fault current
Paralleled generators
  Common Ground Point
  Separate Ground Point

## Slide 43: Generator Considerations: Fault Current
In most generators, the zero-sequence impedance is much less than the positive or negative sequence impedances.
Due to this, resistance grounding must be used unless the generator is specifically designed for solid grounding service.

## Slide 44: Generator Considerations: Common Grounding Point
Generators Grounded through a single impedance must be the same VA rating and pitch to avoid circulating currents in the neutrals
Each Neutral must have a disconnecting means for maintenance as generator line terminals can be elevated during a ground fault.
Not recommended for sources that are not in close proximity

## Slide 45: Generator Considerations: Separate Grounding Points
Separately grounding prevents circulating currents
Multiple NGR’s have a cumulative effect on ground fault current i.e. the total fault current is the sum of all resistor currents plus charging current.
Can be difficult to coordinate tripping or fault location
If total current exceeds about 1000A, single ground point should be considered.

## Slide 46: Reference for further reading:
IEEE 242-2001
IEEE 142-2007
NEC
IEEE 32

## Slide 47: Questions?