## Slide 1: Benchmarking Quasi-Steady State Cascading Outage Analysis Methodologies
IEEE Working Group on Understanding, Prediction, Mitigation and Restoration of Cascading Failures

## Slide 2: Introduction
Planners and operators must ensure the security of power systems
  Must be able to withstand disturbances, to some extent
Traditional way: deterministic criteria
  The power system must be secure against a range of events
  E.g. N-1 security criterion
  Two types of analyses
    Quasi-steady-state (power flow)
    Dynamic
  Various tools with some differences (especially for dynamic analysis), but confidence that they will lead to the (nearly) same conclusions (in the large majority of cases)

## Slide 3: Introduction
Trend to complement (or to replace) deterministic security criteria by probabilistic security criteria
Estimation of the risk for unsecure contingencies?
  Need to simulate what happens after → simulation of cascading outages
Several existing methodologies/tools
Does a power system engineer reach the same conclusions about the risk of cascading outage and the needed remedial actions using the different tools?
  Overall risk, criticalities, etc.
Necessity to benchmark cascading outage analysis methodologies

## Slide 4: Agenda
Introduction
Methodologies
Results
Conclusions & perspectives

## Slide 5: Methodologies

## Slide 6: Methodologies
Classification of methodologies according to the way electrical variables are computed after each cascading event
  Static computation (QSS methodologies)
  Dynamic computation (dynamic methodologies)
  Combination of both (hybrid methodologies)

## Slide 7: Methodologies
Many QSS cascading outage analysis methodologies
  Follow a similar pattern
  But specificities in the implementation…

## Slide 8: Methodologies
Name | Type | Consideration of initiating events | Selection of the ulterior events | Contingency list | Cascading mechanisms
Manchester | R&D | Probabilistic | Probabilistic | Monte Carlo | OL,HF,FI
OPA | R&D | Probabilistic | Probabilistic | Monte Carlo | OL
Practice | R&D | Probabilistic | Probabilistic | Enumeration | OL,HF,VV,FI
PCM | © | Deterministic | Deterministic | Enumeration | OL,VV,VI
Transmission 2000 | © | Probabilistic | Deterministic | Enumeration | OL,VV
PSS/E | © | Probabilistic | Deterministic | Enumeration | OL,VV,VI
TransCare | © | Deterministic | Deterministic | Enumeration | OL,VV,VI
OL=Line Overloads, HF=Hidden Failures, VV=Voltage Violations, VI=Voltage Instability, FI=Frequency Instability

## Slide 9: results

## Slide 10: Results
Test system: IEEE 3-area RTS (1996)

## Slide 11: Results
Metrics
  Expected demand loss
  Distribution of demand loss
    Non-linearity: one large blackout does not have the same impact as multiple events equivalent in EENS
  Distribution of line outages
  Critical lines

## Slide 12: Results
Demand loss
Methodology | Expected demand loss (MW/year)
Manchester | 189.4
DC OPA | 130.7
Practice | 250.5
PSS/E | 79.8
Conditional probability, given that demand loss occurred in the system

## Slide 13: Results
Distribution of line outages

## Slide 14: Results
Critical lines
Different mechanisms modelled, different criteria to select critical lines, …

## Slide 15: Conclusions & perspectives

## Slide 16: Conclusions & perspectives
Results: estimation of the average risk is of the same order of magnitude for the different methodologies, but large variation in distributions and in critical elements
Conclusions about planning and operation actions to take: strongly rely on the specific cascading outage analysis methodology used
  Major barrier hampering the use of assessment of the risk of cascading outage in planning and operation processes
Additional R&D work needed to narrow down the range of results obtained from the different QSS cascading outage methodologies
  Clarification of the simulation objectives (e.g. risk assessment or NERC TPL compliance)
  Cascading phenomena to model, level of detail, uncertainties to consider, linked data and sampling strategies
  Result interpretation and metrics
  Validation with observed cascading statistics